[image: image12.jpg]A= REEN PUMP




       471 US Hwy 250 East, Ashland, Ohio  44805

PH:  419-207-9400    FX:  419-207-8031
	INSTALLATION AND SERVICE INSTRUCTIONS AND REPAIR PARTS LIST FOR 2HP “SEMI-OPEN”

K(H)GS2 CENTRIFUGAL SUBMERSIBLE

GRINDER PUMPS


[image: image1.jpg]



MODELS
	Standard Flow w/ Radial Cutters

	CATALOG NO.
	HP
	PH
	VOLTS
	CORD
	DISCH

	KGS2-2081
	2
	1
	208
	10-5
	1.25

	KGS2-2401
	2
	1
	240
	10-5
	1.25

	KGS2-2083
	2
	3
	208
	14-7
	1.25

	KGS2-2303
	2
	3
	230
	14-7
	1.25

	KGS2-4603
	2
	3
	460
	14-7
	1.25


	High Head w/ Radial Cutters

	CATALOG NO.
	HP
	PH
	VOLTS
	CORD
	DISCH

	KHGS2-2081
	2
	1
	208
	10-5
	1.25

	KHGS2-2401
	2
	1
	240
	10-5
	1.25

	KHGS2-2083
	2
	3
	208
	14-7
	1.25

	KHGS2-2303
	2
	3
	230
	14-7
	1.25

	KHGS2-4603
	2
	3
	460
	14-7
	1.25


	Standard Flow & High Head w/ Radial Cutters INTERNAL CAPACITORS

	CATALOG NO.
	HP
	PH
	VOLTS
	CORD
	DISCH

	KGS2-2081C
	2
	1
	208
	10-3
	1.25

	KGS2-2401C
	2
	1
	240
	10-3
	1.25

	KHGS2-2081C
	2
	1
	208
	10-3
	1.25

	KHGS2-2401C
	2
	1
	240
	10-3
	1.25


	Standard Flow w/ Axial Slicers

	CATALOG NO.
	HP
	PH
	VOLTS
	CORD
	DISCH

	KGSL2-2081
	2
	1
	208
	10-5
	1.25

	KGSL2-2401
	2
	1
	240
	10-5
	1.25

	KGSL2-2083
	2
	3
	208
	14-7
	1.25

	KGSL2-2303
	2
	3
	230
	14-7
	1.25

	KGSL2-4603
	2
	3
	460
	14-7
	1.25


	High Head w/ Axial Slicers

	CATALOG NO.
	HP
	PH
	VOLTS
	CORD
	DISCH

	KHGSL2-2081
	2
	1
	208
	10-5
	1.25

	KHGSL2-2401
	2
	1
	240
	10-5
	1.25

	KHGSL2-2083
	2
	3
	208
	14-7
	1.25

	KHGSL2-2303
	2
	3
	230
	14-7
	1.25

	KHGSL2-4603
	2
	3
	460
	14-7
	1.25


	Standard Flow & High Head w/ Axial Slicers INTERNAL CAPACITORS

	CATALOG NO.
	HP
	PH
	VOLTS
	CORD
	DISCH

	KGSL2-2081C
	2
	1
	208
	10-3
	1.25

	KGSL2-2401C
	2
	1
	240
	10-3
	1.25

	KHGSL2-2081C
	2
	1
	208
	10-3
	1.25

	KHGSL2-2401C
	2
	1
	240
	10-3
	1.25


Read all instructions in this manual before operating pump.

[image: image13.jpg]Please Read This Before installing Or Operating Pump.

This information is provided for SAFETY and to PREVENT
EQUIPMENT PROBLEMS_ To help recognize this information,
observe the following symbols:

personal injury orindicates factors concemed with
assembly, installation, operation, or maintenance which
‘could result in damage to the machine or equipment if

i IMPORTANT! Warns about hazards that can result

ignored.

CAUTION ! Warns about hazards that can or will cause minor
personal injury or property damage if ignored. Used with symbols
below.

WARNING | Warns about hazards that can o will cause serious
personal injury, death, or major property damage if ignored, Used
with symbols below.

|

Hazardous fluds car
sauss fire or explo-
sions, bumes or death
coud result

Extremely ot - Severe
burnes can occur on contact.

Hazardous fluids can Hazard-
ous pressure, erptions or ex-
plosions could cause personal
injury or property damage.

Hazardous voltage can
| shook, burn or catse death

Only qualified personnel should install, operate and repair
pump. Any wiring of pumps should be performed by a qualified
slectrician.

| Biohazard can cause
serious personal ijury.

Rofating machinery
1 w Amputation or severe
| R faceration can result.

WARNING ! - To reduce risk of electrical shock, pumps.
and control panels must be properly grounded in
accordance with the National Electric Gode (NEC) or
the Canadian Electrical Code (CEC) and all applicable
state, provincs, local codes and ordinances.

WARNING! - To reduce risk of electrical shock, always
disconnect the pump from the power source before
handiing or servicing. Lock out power and tag.

Prevent large articles of clothing, large amounts of chemicals,
otfier materials or substances such as are uncomman in
domestic sewage from entering the syster.

During power black-outs, minimize water consumption ai the
home(s) to prevent sewage from backing up into the house.

Alweays keep the shut-off valve completely apen when system is
in operation (unless advised otherwise by the proper authorities).
Before removing the pump from the basin, be sure to close the

shut-off valve. (This prevents backflow from the pressure sewer.)

Keep the control panel lacked or confined to prevent
unauthorized accessto it.

Ifthe pump is idle for long periods of time, it is advisable to start
the pump occasionally by adding water to the basin.

CAUTION! Pumps build up heat and pressure
dusing operation-allow time for pumps to cool
before handiing or servicing.

WARNING! - DO NOT pump hazardous materials
(fammable, caustic, etc.) unless the pump is specifically

designed and designated to handle them.

Do not black or restrict discharge hose, as discharge hose may
whip under pressure.

WARNING! - DO NOT wear loose clothing that may
become entangled in the impsler or other moving parts.

'} WARNING! - Keep clear of suction and discharge
openings. DO NOT insert fingers in pump with power
connected.

Wake sure lifting handles are securely fastened each time before
Iifting. Do not operate pump without safety devices in place.
Always repiace safety devices that have been removed during
service or repair.

Da not exceed manufacturers recommendation for maximum
performance, as this could cause the motor to overheat.

Secure the pump in its operating position so it can not tip over,
fall or slide.

Cable should be protectad at all times to avoid punctures, cut,
bruises and abrasions - inspect frequently.

Never handle connected power cords with wet hands.

To reduce risk of electrical shock, all wiring and junction
connections should be made per the NEC or CEC

and applicable state or province and local codes.
Requirements may vary depending on usage and
focation.

Submersible Pumps are not approved for use in
swimming pools, recreational water installations,
decorative fountains or any installation where human
‘contact with the pumped fluid is common,

Do not remove cord and strain relief. Do not connect conduit to
pump.

Products Retumed Must Be Cleaned, Sanitized, Or
Decontaminated As Necsssary Prior To Shipment, To
Insure That Employees Will Not Be Exposed To Health
Hazards In Handiing Said Material. All Applicable Laws
And Reguiations Shall Apply.

Bronze/brass and bronze/brass fitted pumps may
contain lead levels higher than considered safe for
potable water systems. Various government agencies
have determined that leaded copper alloys should not
be used in potable water applications. For non-leaded
copper alioy materials of construction, piease contact
factory.




Most accidents can be avoided by using COMMON SENSE.

KEEN PUMP  is not responsible for losses, injury or death resulting from a failure to observe these safety precautions, misuse, abuse or misapplication of pumps or equipment.


PUMP SPECIFICATIONS:

SPECIFICATIONS

WIRING DIAGRAMS
(Internal Capacitors)

SINGLE PHASE, 208/240V, 10/3 CABLE

[image: image2.emf]
	WIRES
	OHM 208V
	OHM 240V

	WHITE (1)
	BLACK (3)
	1.0
	1.6


SINGLE PHASE, 208/240V, 10/5 CABLE


[image: image3.emf]
	WIRES
	OHM 208V
	OHM 240V

	WHITE (1)
	BLACK (3)
	1.0
	1.6

	WHITE (1)
	RED (2)
	6.2
	6.8

	BLACK (3)
	RED (2)
	5.2
	5.2


3-PHASE, 208/230/460V, 14/7 CABLE

[image: image4.emf]
	WIRES 230 VOLT
	OHM

	WHITE
	BLACK 
	

	WHITE 
	RED
	

	BLACK
	RED
	

	WIRES 460 VOLT


	

	WHITE
	BLACK 
	

	WHITE 
	RED
	

	BLACK
	RED
	


PUMP SPECIFICATIONS

DISCHARGE...................................
1-1/4” NPT OR 2-Bolt Flange, Vertical

LIQUID TEMPERATURE................
120 degrees F (Continuous)

                                                      
140 degrees F. (Intermittent)

MOTOR HOUSING..........................
Cast Iron, ASTM A-48, Class 35
CORD CAP......................................
Cast Iron, ASTM A-48, Class 35
VOLUTE..........................................
Cast Iron, ASTM A-48, Class 35
SEAL PLATE...................................
Cast Iron, ASTM A-48, Class 35
IMPELLER.......................................
440C StainlessSteel (Hardened Available)
                                                 
10 vane, Semi-Open with Pump-out Vanes, Dynamically Balanced

SHREDDING RING (Cutter)...........
Hardened 440C Stainless Steel

                                                     
56-60 Rockwell C 

GRINDER IMPELLER (Cutter).......
Hardened 440C Stainless Steel

                                                       
56-60 Rockwell C 

RETAINER PLATE (Slicer).............
Hardened 440C Stainless Steel

                                                      
56-60 Rockwell C 

SLICER IMPELLER (Slicer)...........
Hardened 440C Stainless Steel

                                                     
56-60 Rockwell C 

SHAFT.............................................
416 Stainless Steel

SHAFT SEAL..................................
Mechanical
Main (Motor)


Secondary (Pump)
                                                                        

Silicon Carbide – Rotating Face
Silicon Carbide – Rotating Face    

                                                                        

Silicon Carbide – Stationary Face
Silicon Carbide – Stationary Face  

                                                   
Nitrile - Elastomer

                                                     
300 Series Stainless Steel - Hardware

BEARING (UPPER).........................
Single Row, Ball, Oil Lubricated

BEARING (LOWER)........................
Single Row, Ball, Oil Lubricated
SLEEVE BEARING.........................
Bronze with Oil Groove
HARDWARE....................................
300 Series Stainless Steel

O-RINGS..........................................
Buna-N

CORD..............................................
10-3 AWG, Type SOOW (“C” Model)





10-5 AWG, Type SOOW (Single Phase)





14-7 AWG, Type SOOW (Three Phase)
                                                       
30’Length Standard. Other Lengths Available.

CORD ENTRY.................................
Watertight Sealed Design

                                        

Agency-Approved, Watertight Strain Relief Cord Grip – Outer Jacket Seal

                                                   
Epoxy Potted – Inner Conductor Seal

MOTOR (SINGLE PHASE).............
2 HP, 3450 RPM, 60 Hz

                                                   
208 or 240 volts Available
                                                    
Includes Overload Protection in the Motor.

                                                      
Oil Filled, Class N
                                                      
Capacitor Start / Capacitor Run




Start Capacitor

Run Capacitor 

208 & 240 Volt Models...................
216-259 mfd, 250 VAC

50 mfd, 370 VAC 

MOTOR (THREE PHASE)...............
2 HP, 3450 RPM, 60 Hz

                                                  
Tri-voltage, 208 / 230 / 460 volts      

                                                  
On-Winding temperature sensor, requires temperature sensor circuitry

                                                   
in control panel

                                                   
Oil Filled, Class N
OPTIONAL EQUIPMENT................
Seal Materials

                                                     
Additional Cable Lengths

                                                 
Impeller Trims

Installation


TROUBLESHOOTING

The troubles listed below are potential problems involving the pump. Other troubles can occur from faulty control box operation. Consult control box instructions for troubleshooting list involving the control box.

PROBLEM               
PROBABLE CAUSE
Pump will not run.                  
Tripped breaker, blown fuse, poor electrical connection, interruption of 

                                                     
power, improper power supply.

                                                       
Float switch defective or restricted.

                                                      
On single phase pumps, electronic start switch or capacitors blown.

                                                       
Overload in motor tripped.

                                                      
Solid material lodged in pump inlet.

Pump runs, but does not          
Pump impeller may be air locked. Start and stop pump several times to
pump liquid from basin.             
purge air. Check to ensure vent hole in volute is open and clean.

                                                       
Lower “OFF” float may be set too low, allowing air into pump.

                                                       
Pump inlet or valves in discharge pipe may be clogged.

                                                        
Discharge valve may be closed.

Pump hums, but does not run.   
Incorrect voltage.
                                                       
Pump inlet plugged.

                                                        
Cutter jammed or loose on shaft, worn or damaged.

Pump delivers low volume         
Low voltage.
of water.                                          
On three phase pumps, motor running backwards.

                                                       
Discharge restricted.

                                                        
Check valve stuck closed or installed backwards.

                                                        
Pump motor damaged / worn.

                                                        
Pump may be air locked.

                                                        
Cutter loose or jammed on shaft, worn or damaged.

Pump is noisy.                             
Grinder impeller may be rubbing against grinder ring due to  

                                                        
misalignment, bent shaft or object stuck in impeller.

                                                       
Grinder assembly may be partially clogged.

                                                      
Pump cavitation due to low discharge pressure.

Pump cycles frequently.               
Check valve stuck closed or installed backwards.

                                                         
Ground water entering basin.

                                                        
Fixtures are leaking.

Pump will not turn off.                 
Float switch defective or movement restricted.

                                                       
H-O-A switch in panel is in “HAND” position.

                                                       
Pump may be air locked.

                                                        
Excessive inflow / pump not sized for the application.

Grease and solids                         
Pump “ON” switch may be set too high.     

accumulated in basin and            
Debris may have accumulated around lower float weight causing pump
will not pump out.                         
to turn off too soon. Clean debris away from weight and cord.
Red light illuminated at                
Moisture detection in double seal pumps indicating service is required.   

control box.                                   
Lower seal has failed. Secondary seal still functioning.

Circuit breaker trips.                     
Electrical short to ground.

                                                       
Check troubleshooting in control panel before pulling pump.

                                                        
Check all electrical cords for damage.

                                                        
Pull pump and take resistance readings of motor to determine if problem

                                                       
is in the pump or control box.

REPLACING GRINDER IMPELLER AND SHREDDING RING “RADIAL CUTTERS”
Note: This is the only disassembly operation permitted in the field.

          All other repairs must be performed at an authorized service center or the factory.

[image: image5.png]



STANDARD TOOLS REQUIRED:

· Standard socket wrench set.

· Standard set of open end wrenches.

· Hammer.

· Vise grip pliers.

· Allen head socket set.

· Screwdrivers.

· Wire brush.

CAUTION – Disconnect all power and control wires to motor at the control panel before starting

the disassembly operations. Do not rely upon opening the circuit breaker only.

IMPORTANT – Pump should be sanitized with bleach before starting work.
Pump should be thoroughly cleaned of trash and deposits before starting 

                         
disassembly operations.

                         
Wear protective gloves and clothing.

                         
Always use a rag on the impeller when turning to prevent cutting hands on the 

                         
sharp edges of the shredding ring.

DISASSEMBLY OF SHREDDING RING AND GRINDER IMPELLER

1. Hold the grinder impeller by prying against the impeller cutting bar and remove the allen head cap screw from the end of the shaft.

2. Use a large screwdriver in the slot end of the shaft and tap (counterclockwise) on one of the large cutter vanes with a hammer. Tap in a counterclockwise direction (thread is right hand).

3. If the impeller removes easily, clean and replace if worn.

4. Make sure the pump impeller has not loosened when the grinder impeller was removed. This can be checked on reassembly of grinder impeller and shredding ring. The tips of the impeller cutter vanes should extend 1/8” below the bottom of the shredding ring. If the distance is greater, the pump impeller has loosened. If the distance is less, the shredding ring is not properly seated.

5. After the volute case has been removed, insert screwdriver in slot end of shaft and tap hammer against the outer vane of the ductile iron pump impeller (clockwise) to ensure it is threaded tight against shoulder on shaft.

6. Use large screwdriver to tap stainless steel cutter ring from cast iron volute.

7. Clean all threads with a wire brush and file smooth any nicked threads. Use NEVER-SEEZE or other graphite compound on threads before replacing grinder impeller.

8. Make sure allen head cap screw in bottom of pump shaft is tight. Make sure the impeller turns freely by hand after reassembly. Some drag will be present due to the shaft seals. There should not be any binding or tight spots when turning the grinder impeller.
REPLACING IMPELLER AND RETAINER PLATE “AXIAL SLICERS”
Note: This is the only disassembly operation permitted in the field.

          All other repairs must be performed at an authorized service center or the factory.

[image: image6.png]



STANDARD TOOLS REQUIRED:

· Standard socket wrench set.

· Ball-peen Hammer.

· Feeler Gauges (minimum range .008-.012 inches)

· Vise grip pliers.

· Allen head socket set.

· Screwdrivers.

· Wire brush.

CAUTION – Disconnect all power and control wires to motor at the control panel before starting

the disassembly operations. Do not rely upon opening the circuit breaker only.

IMPORTANT – Pump should be sanitized with bleach before starting work.

                         
Pump should be thoroughly cleaned of trash and deposits before starting 

                         
disassembly operations.

                         
Wear protective gloves and clothing.

                         
Always use a rag on the impeller when turning to prevent cutting hands on the 

                         
sharp edges of the impeller and slicer plate.

DISASSEMBLY OR REPLACING OF SLICER PLATE AND SLICER IMPELLER

1. Remove Slicer retainer (3 bolts).

2. Use a ball-peen hammer to tap onto (3 blade) rotary slicer impeller.  Tap in a counterclockwise direction (thread is right hand).

3. Remove “disk-shaped” slicer plate.  May have to pry with screwdriver.
4. Once slicer plate is removed, shims will be visible on threaded shaft.

5. Slicer parts can now be cleaned and reassembled or replaced.
6. If discarding all shims, you must use new shims from shim kit.
7. Place (Qty:2) .01 inch shims onto threaded shaft, making certain to align keyway of stock with shaft.

8. Place new or cleaned slicer plate onto threaded shaft, making sure shims stay in place along keyway.
9. Place new or cleaned rotary (3 blade) slicer impeller onto threaded shaft, turning (Clockwise).

10. Rotate onto shaft with hands until snug.  Use ball-peen hammer to lock onto shaft.

11. IMPORTANT: USING FEELER GAUGES, CHECK DISTANCE BETWEEN SLICER PLATE AND SLICER IMPELLER.  DISTANCE TOLERANCE (.008-.012 INCHES).

12. If tolerance is satisfactory, go to step 13.  If tolerance is beyond or under range, go back to step 7.
13. Place new or cleaned slicer retainer onto volute bottom.
14. Make sure the impeller turns freely by hand after reassembly. Some drag will be present due to the shaft seals. There should not be any binding or tight spots when turning the slicer impeller.

START KIT REPLACEMENT “C” MODEL
1. Place pump in upright position.

2. Loosen cord cap retaining bolts (1). Keen recommends that a rag or towel be wrapped around the joint where the cord cap and bearing housing meet.

3. Slowly move cord cap upward until any pressure that may be present is released, remove the retaining bolts and lift off cord cap.

4. Remove resistor mounting screws (2) and replace resistor as required. Wire per attached diagram and reinstall.
5. Remove start switch (3) mounting screw and replace start switch as required. Wire per attached diagram and reinstall.
6. Remove bracket mounting screws (4) as required, to lift entire assembly from casting.
7. Remove capacitor screw from backside of dual bracket (5) and replace start/run capacitors as required.
8. Clean mating surfaces and inspect O-Ring for cuts or damage (replace if necessary). Reinstall cord cap.

9. Check power cord at plug with ohm meter for shorts to ground.

[image: image7.jpg]




[image: image8.emf]
REPAIR PARTS LIST

[image: image9.emf]

[image: image10.emf]
	
	Pump Model Numbers w/ Axial Slicers
	KGSL2-2081/2301/2401(C)

KHGSL2-2081/2301/2401(C)
	KGSL2-2083/2303/4603

KHGSL2-2083/2303/4603

	REF. #
	DESCRIPTION
	QTY.
	PART NUMBER
	QTY.
	PART NUMBER

	
	Castings
	
	
	
	

	1
	Bearing Plate, Upper, Cast Iron
	1
	KGA2070-5-02
	1
	KGA2070-2-02

	1
	Assembly, Upper Bearing Plate “C” Models
	1
	KGA2070-5-02
	-
	-

	2
	Housing, Lower Bearing, Cast Iron
	1
	K0467-2-01
	1
	K0467-2-01

	3
	Seal Plate, Lower, Cast Iron (w/ bushing)
	1
	K0447-5-01
	1
	K0447-5-01

	4
	Volute Case, Cast Iron
	1
	K0444-2-01
	1
	K0444-2-01

	5
	Adapter, Discharge, Vertical, 1-1/4" NPT, Cast iron
	1
	K0448-2-01
	1
	K0448-2-01

	
	Repair parts
	
	
	
	

	7
	Seal, Shaft, Lower and Upper, Sil. Carbide, Type 21
	2
	KG2172
	2
	KG2172

	8
	O-Ring, Buna-N, Motor, Cord Cap, Brg. Hsg.,5-7/8 OD
	4
	KG2010
	4
	KG2010

	9
	O-Ring, volute adapter, Buna-N, 6.234 ID
	1
	K0166-1-08
	1
	K0166-1-08

	10
	Bearing, Ball, Upper Ball, 1.575OD
	1
	KG2003
	1
	KG2003

	11
	Bearing, Ball, LOWER, 2.047OD
	1
	KG2009
	1
	KG2009

	
	Hardware & Miscellanies parts
	
	
	
	

	12
	Screw, Cap, 1/2-13UNC x 1" LG, SST
	2
	CS1/2X1SS
	2
	CS1/2X1SS

	13
	Screw, Cap, 5/16-18UNC x 1-3/4" LG, SST
	4
	CS5/16X1-3/4SS
	4
	CS5/16X1-3/4SS

	14
	Screw, Cap, 5/16-18UNC x 1-1/4" LG, SST
	4
	CS5/16X1-1/4SS
	4
	CS5/16X1-1/4SS

	15
	Screw, Cap, 5/16-18UNC x 1-1/2" LG, SST
	4
	CS5/16X1-1/2SS
	4
	CS5/16X1-1/2SS

	16
	Screw, Cap, 10-32UNC x 5/8" LG, SST
	1
	CS10X5/8SS
	1
	CS10X5/8SS

	17
	Screw, RD Head, Drive, #4-7UNC x 1/4 “ LG, SST
	6
	DS4X1/4SS
	6
	DS4X1/4SS

	18
	Screw, Cap, C-sunk, 1/4-20UNC x 5/8" LG, SST
	3
	K0317-1-02
	3
	K0317-1-02

	19
	Screw, Skt Hd, (Allen) 1/4 -20UNC x 3/4 “ LG, SST
	1
	SCS1/4X3/4SS
	1
	SCS1/4X3/4SS

	20
	Washer, Impeller, KGS series
	1
	K0451-1-01
	1
	K0451-1-01

	21
	Retaining Ring,  Disc, 2hp slicer impeller, SST
	1
	K0558-3-01
	1
	K0558-3-01

	22
	Shim, 5/8” ID x 1.00” OD x .005, SST
	2
	K0458-1-04
	2
	K0458-1-04

	23
	Nameplate,  Motor
	1
	KNP0001
	1
	KNP0001

	24
	Handle, Lifting, SST
	1
	KG2017
	1
	KG2017

	25
	Oil, Dielectric
	56 oz
	K0737-1-01
	56 oz
	K0737-1-01

	26
	Assembly, Housing & Stator 208 Volt 1 ph
	1
	KGA2097-5-200
	-
	-

	26
	Assembly, Housing & Stator 240 Volt 1 ph
	1
	KGA2097-5-100
	-
	-

	26
	Assembly, Housing & Stator 208/230/460 Volt 3 ph
	-
	-
	1
	KGX2098

	
	Housing, motor, Cast iron
	1
	KGA2006-2-01
	1
	KGA2006-2-01

	
	Stator 208 Volt 1 ph
	1
	K0476-1*
	-
	-

	
	Stator 240 Volt 1 ph
	1
	K0477-1*
	-
	-

	
	Stator 208/230/460 Volt 3 ph
	-
	-
	1
	KG2013*

	27
	Assy, Cord Cap, 30 ft. length cord.  10/5
	1
	KGX2099-105-30
	-
	-

	27
	Assy, Cord Cap, 30 ft. length cord.  10/3 “C” Model
	1
	KGX2099-103-30
	-
	-

	27
	Assy, Cord Cap, 30 ft. length cord.  14/7
	1
	-
	1
	KG2099-14730

	28
	Rotor and shaft assembly, 1 & 3 phase , Hazloc
	1
	K0483-5-01*
	1
	K0483-5-01*

	29
	Pre-insulated Crimp Wire Conn. 6LU60 (“C” Pump)
	2
	WC2-14
	-
	-

	29
	Pre-insulated Crimp Wire Conn. 6LU60 (1 ph)
	4
	WC2-14
	-
	-

	29
	Pre-insulated Crimp Wire Conn. 6LU60 (3 ph, 230V)
	-
	-
	7
	WC2-14

	29
	Pre-insulated Crimp Wire Conn. 6LU60 (3 ph, 460V)
	-
	-
	9
	WC2-14

	30
	Impeller, SST, High Flow, 5.50” Dia.
	1
	K0464-2-02
	1
	K0464-2-02

	30
	Impeller, SST, High Head, 6.50” Dia.
	1
	K0464-2-01
	1
	K0464-2-01

	31
	Plate, Slicer, SST, High Flow
	1
	K0452-2-01
	1
	K0452-2-01

	31
	Plate, Slicer, SST, High Head
	1
	K0452-2-200
	1
	K0452-2-200

	32
	Impeller, Slicer, 3-Blade, SST
	1
	K0454-2-100
	1
	K0454-2-100

	33
	Plug, 1/4 NPT pipe, SST  (“C” Pump)
	4
	PLUG1/4
	-
	-

	33
	Plug, 1/4 NPT pipe, SST  (All Others)
	3
	PLUG1/4
	3
	PLUG1/4

	34
	Wire, Moisture Detector
	1
	K0142-1-01
	1
	K0142-1-01

	35
	Sensor, Moisture
	1
	K0141-5-04
	1
	K0141-5-04

	36
	Capacitor, Start, 216-259 Mfd, 250 VAC
	1
	K0408-1-02
	-
	-

	37
	Capacitor, Run, 50 Mfd, 370 VAC
	1
	K0341-1-01
	-
	-

	38
	Assembly, Start switch (230V)
	1
	K0653-5-01
	-
	-

	40
	Washer, Lock, 3/8” SST
	2
	LWASH3/8SS
	2
	LWASH3/8SS

	41
	Screw, Cap, 3/8-16UNC x 1” LG, SST
	2
	CS3/8X1SS
	2
	CS3/8X1SS

	42
	Plate, Slicer retainer, SST
	1
	K0453-1-01
	1
	K0453-1-01

	43
	Shim, 5/8” ID x 1.00 OD x .010 Thk.
	2
	K0458-1-03
	2
	K0458-1-03

	44
	Nameplate, Keen (Not pictured)
	1
	KNP0003
	1
	KNP0003


* After Jan-19 - Add F suffix

               471 US Hwy 250 East, Ashland, Ohio   44805

    PH:  419-207-9400    FX:  419-207-8031

Limited Warranty

During the time periods and subject to the conditions hereinafter set forth, Keen Pump will repair or replace to the original user or consumer, any portion of your new Keen product which proves defective due to defective materials or workmanship of Keen Pump.  Contact your closest authorized Keen Pump representative or distributor for warranty service.  At all times, Keen Pump shall have and possess the sole right and option to determine whether to repair or replace defective equipment, parts or components.  Damage caused by acts of GOD or conditions beyond the control of Keen Pump is not covered by this warranty.

WARRANTY PERIOD:

36 months from date of manufacture.

Start-up reports are required to support warranty claims.  Warranty effective only if Keen Pump supplied or authorized control panels are used.  Single phase pumps must utilize Keen Pump supplied start components.

THIS WARRANTY WILL NOT APPLY:

(1) To defects or malfunctions resulting from failure to properly install, operate or maintained the product in accordance with printed instructions provided.

(2) To failures resulting from abuse, accident or negligence.

(3) To normal maintenance services and the parts used in conjunction with such service.

(4) To products which are not installed in accordance with applicable local codes, ordinances and good trade practices.

(5) The product is used for purposes other than for what is was designed and manufactured.

(6) If 3 phase motors are installed on a single phase power supply using a phase converter or if 3 phase power is supplied by only two transformers, making an open Delta system.

WARRANTY EXCLUSIONS:

Keen Pump specifically disclaims the implied warranties of merchantability and fitness for a particular purpose after the termination of the warranty period set forth herein.  No warranties or representations at any time made by any representatives of Keen Pump shall vary or expand the provision hereof.

LIABILITY LIMITATION:

In no event shall Keen Pump be liable or responsible for consequential, incidental or special damages resulting from or related in any manner to any Keen Pump product or parts thereof.  Personal injury and/or property damage may result from improper installation.  Keen Pump disclaims all liability, including liability under this warranty, for improper installation.  Keen Pump recommends following the instructions in the installation manual.  When in doubt, consult a professional.  Some states do no allow the exclusion or limitation of incidental or consequential damages, so the above limitation or exclusion may not apply to you.

LABOR, ETC., COSTS:

Keen Pump shall in no event be responsible or liable for the cost of field labor or other charges incurred by any customer in removing and/or reaffixing any Keen Pump product, part or component thereof or any temporary pumping of other equipment.

RETURNED OR REPLACED COMPONENTS:

Any item to be replaced under this Warranty must be returned to Keen Pump, or such other place as Keen Pump may designate, freight prepaid.

This warranty gives you specific legal rights and other rights which may vary from state to state.

In the absence of suitable proof of this purchase date, the effective date of this warranty will be based upon the date of manufacture.  Example:  1605 = Year-Month = 2016, May.                                                                     P/N O&M-K(H)GS2
[image: image11.emf]Model HPMax. FlowMax. HeadHomes (EDUs)Gallons/DayHomes (EDUs)Gallons/Day

KPCG 1 15 * 2 800 4 1600

LCG2 2 59 116

KG2 2 43 106 4 1600 8 3200

KHG2 2 20 130 3 1200 6 2400

KHHG2 2 30 160 3 1200 6 2400

KHHG2H 2 28 225 3 1200 6 2400

KG3 3 183 65 12 4800 25 10000

KG5 5 190 87 25 10000 50 20000

KHG3 3 100 105 6 2400 12 4800

KHG5 5 100 140 8 4000 16 8000

KHG7 7.5 100 170 10 4800 20 10000

KG10 10 185 160 25 10000 50 20000

* KPCG 1hp Progressive Cavity pump Max Head based on Minimum Flow requirements

Minimum Flow = 6 GPM 

Maximum Head = 225 TDH

Simplex Duplex

Keen Pump Grinder Recommended Limits of Application


WARNING !


Any wiring to be done on pumps should be done by a qualified electrician.





NEVER operate a pump with a power cord that has frayed or brittle insulation.





NEVER let cords or plugs lay in water.





NEVER handle connected power cords with wet hands.





NEVER be in contact with the liquid being pumped while pump cord is connected to electrical supply.





Only qualified personnel should install, operate or repair pump.





* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *


* * * * * * * * * USE AND CARE * * * * * * * * * * * * 


DO NOT pump hazardous material not recommended for pump. NEVER introduce:


Explosives


Flammable Material


Lubricating Oil and/or Grease


Chemicals, Solvents, etc.


Gasoline


Any Petroleum Product





Regulatory agencies advise that the following items should not be introduced into any sewer:


Glass


Metal


Diapers


Clothing, socks, rags, etc.


Plastic objects (toys, utensils, etc.)


Sanitary napkins or tampons





DO NOT pump without safety devices in place.





For hazardous locations, use pumps listed and classified for such locations.





DO NOT use non-explosion rated pumps in locations considered hazardous in accordance with the National Electric Code, ANSI/NFPA 70-1993.





IMPORTANT!


KEEN PUMP is not responsible for losses, injury or death resulting from failure to observe these safety precautions.





WARNING!


THE PUMP MUST BE WIRED BY A QUALIFIED ELECTRICIAN, USING AN APPROVED STARTER BOX AND SWITCHING DEVICE. 





On 3 phase pumps only, “Motor Protection” must be provided by the installer. All 3 phase pumps must be installed with magnetic starters having 3 leg overload protection in accordance with the NEC (National Electric Code). For duplex installations, both pump motors must have separate overload protection.





Pumps with seal leak detectors must be connected to the proper control circuitry.





DANGER!


HAZARDOUS MOVING PARTS. To reduce risk of injury, disconnect power before servicing. Never put fingers near grinder impeller or in pump inlet when pump cord is connected or pump is operating.





For use with maximum 140 degrees F liquid. 





DANGER!


In the initial installation, before sewage is admitted to the basin, there is no danger on entering the basin. AFTER SEWAGE HAS BEEN IN THE BASIN, THERE IS DANGER. Sewage water produces methane and hydrogen sulfide gasses, both of which are highly poisonous. A breathing device may be required. Never enter the basin unless cover is open and outside blower is used to force fresh air into the basin. Also the worker in the basin must wear a harness attached to the surface so he can be pulled out in case of asphyxiation.


NEVER WORK ALONE!





WARNING!


Do not exceed working load limit of lifting chain, cable or rope. Do not use lifting chain, cable or rope where failure could result in loss of life.





Examine all lifting devices, chain, cable or rope for damage before and after each lift. Do not use any lifting devices that are not rated for and designed to lift the weights involved with these pumps. DO NOT LIFT PUMP BY POWER CORD.





Do not install or remove pump with person(s) in the basin.





This pump is designed to handle materials which could cause illness or disease through direct exposure. Wear and use protective clothing when working on the pump or piping.





USAGE:


The 2 HP grinder pumps are for pumping domestic sewage. One pump can handle the sewage from a maximum of 2 homes. 





These pumps are not to be used for pumping commercial or industrial sewage from factories, schools, motels, apartments, etc..





This pump is intended to grind and pump all normal sewage for home use. It will handle reasonable quantities of disposable diapers, sanitary napkins, paper towels, rubber material, wood, cigarette butts, string, plastic and other material not normally found in sewage.





CAUTION!


Pump is not to be disassembled in the field except at certified service stations or at the factory. Warranty is void if pump is taken apart for any reason other than to replace grinder impeller and grinder ring, which is covered in these instructions.





PACKAGING


Each pump is packaged with 30 feet of power cord in a carton that is marked with the Model Number. Longer cords are available – consult factory.





INSPECTING PUMP


Before making any piping or electrical connections, check pump for any shipping damage. Turn grinder impeller to be sure it is free. DO NOT TURN IMPELLER WITH FINGERS AS EDGES ARE SHARP. Use allen wrench in the impeller screw to turn the impeller.





CAUTION!


No persons should be in the basin when pump is lowered into position! DO NOT lift pump in a manner where failure could result in loss of life.





After pump is installed in basin, NEVER WORK ON MOTOR OR GRINDER UNIT WITHOUT DISCONNECTING MOTOR LEAD WIRES FROM CONTROL PANEL. DO NOT RELY UPON OPENING THE CIRCUIT BREAKER ONLY!





ELECTRICAL:


MOTOR OVERLOAD PROTECTION


Single phase motors are provided with an on-winding thermal overload switch. If motor overloads or overheats for any reason, the switch opens, stopping motor. As soon as the motor cools to normal temperature, the switch automatically closes and restarts motor.





MOISTURE DETECTION


All 2 HP, dual seal grinder pumps with external start kit or 3-phase, contain an electrode for detecting water within the unit. The electrode is housed within the secondary seal chamber, isolated from the motor chamber. If the electrode detects water within the oil-filled housing, it will close the circuit to the red alarm light in the control panel, indicating the pump must be serviced before the upper seal fails.





MOTOR POWER CORDS 


Pump models with seal leak detector, single phase use a 10AWG-5C cord, three phase use a 14AWG-7C cord. Models without seal leak use a 10AWG-3C cord. The three power conductors are BLACK, WHITE and RED. The ORANGE conductor connects to the seal leak probe and GREEN conductor connects to the ground screw inside the cord cap. 


For single phase,


BLACK is “Common”


WHITE is “Run”


RED is “Start”.





IMPORTANT!


Ground wires must be connected in the control box to grounding bar, which is connected to a good suitable ground. MOTOR IS NOT SAFE UNLESS PROPERLY GROUNDED.





IMPELLER ROTATION: When looking at the bottom of the pump and through the inlet of the volute, rotation of the impeller is COUNTER-CLOCKWISE.








P/N O&M-K(H)GS2

Effective Jan 2025


21
  Jan 2025

_1526472194.unknown

_1526472333.unknown

_1558332110.unknown

_1526471331.unknown

_1523958040.unknown

